## Slide 1: Techno-Economic Analysis of Voltage Sag Mitigation with Renewable Energy Sources and Storage devices
S. V. Kulkarni
Indian Institute of Technology Bombay
svk@ee.iitb.ac.in
Panel Session “Smart Grid Technology”: 19PESGM3460

## Slide 2: An Indo-Australian Joint-Partnership
Collaboration initiated through visits of IIT Bombay faculty to University of Wollongong and vice-versa in 2013.
MoU signed between IITB and UOW in Apr. 2014
  Includes academic visits, joint research projects and joint supervision, exchange of information, joint conferences, seminars, workshops and student exchange programs.
One of the PhD students from IITB, Subir Majumder, had registered under the joint PhD scheme between UOW and IITB.
  He visited UOW for 18 months in 2016-2017.
Mr. Majumder has recently submitted his PhD thesis for evaluation.

## Slide 3: Overview of the Presentation
Use of smart grid technologies on the traditional topological framework of the distribution networks has the following challenges:
  Intrinsic variability of RE sources
  Weak correlation between them and loads for variability mitigation
  Radial nature of the network  single point of failure  increases vulnerability to faults
  Increased penetration of the inertia-less inverter-interfaced generators  reduced rotational inertia of the entire system
A few aspects of these challenges are considered as the objectives of the joint PhD and will be discussed in this presentation

## Slide 4: Sizing, Placement, and Scheduling, of Storage Devices

## Slide 5: RE Variability Mitigation
Ramp-rate limits of conventional thermal generators are impediments
Storage devices offer attractive solutions for variability mitigation
For increased penetration of storage devices:
  Proper remuneration and incentivization of operational benefits
  Resources for energy arbitrage should be adequately available
RE-storage devices based generation scheme can limit price volatility
Some amount of base-load generation is preferable
  Variability mitigation solely based on price arbitrage opportunity would drive the price of electricity high

## Slide 6: Problem 1A: Sizing of Battery Storage Devices (BSDs)
Objective: Sizing of the BSDs to minimize variability injection (daily injection of RE-BSD ~ constant) with overall cost optimized
Hypothesis from literature: In a multi-type storage devices system:
  Low-frequency component of load-generation imbalance to be taken care by low-cost finite cycle batteries
  High life-cycle batteries cater to the high-frequency component of load-generation imbalance
A better criterion is to minimize unit cost to throughput factor
Discrete Fourier transform-Inverse discrete Fourier transform and the cut-off frequency segregates high- and low-frequency components within a dataset
S. Majumder, S. A. Khaparde, A. P. Agalgaonkar, P. Ciufo, S. Perera, and S. V. Kulkarni, “DFT-Based Sizing of Battery Storage Devices to Determine Day-Ahead Minimum Variability Injection Dispatch With Renewable Energy Resources,” IEEE Trans. Smart Grid, vol. 10, no. 1, pp. 626-638, Jan. 2019.
S. Majumder, S. A. Khaparde, A. P. Agalgaonkar, P. Ciufo, S. Perera, and S. V. Kulkarni, “DFT-based sizing of battery storage devices to determine day-ahead minimum variability injection dispatch with renewable energy resources,” in 2018 IEEE Power & Energy Society General Meeting (PESGM), Portland, OR, 2018, pp. 1-1.

## Slide 7: DFT/IDFT Technique
Imbalance
Notes: Fig. DFTIDFT

## Slide 8: Problem Formulation
Notes: Fig. BSDSizing2

## Slide 9: Solution of the Optimization Problem
The solution space (the cut-off frequency) is discrete, and to obtain an optimal solution, a mode-pursuing sampling method has been utilized
Observations:
  Application of two types of BSDs in conjunction need not result in the most economic planning
Notes: Fig. CostArbit

## Slide 10: Benefit of 3σ Planning
Observation:
  Exponential reduction of the injection of variability into the grid with increasing statistical significance (standard deviation)

## Slide 11: Problem 1B: Sizing of Battery-Supercapacitor Storage Devices
Limited life-cycle, lower power density limits the use of batteries, however, these deficiencies are complemented by supercapacitors
However, supercapacitors suffer from high self-discharge and high energy cost
Objective: Calculate an optimal cut-off frequency separating the low- and high-frequency components for minimum variability injection that leads to an optimal annualized cost
Constraints:
  Use supercapacitors to mitigate the high frequency variability (frequent charging-discharging), iff the cut-off frequency is more than certain number, and the annualized cost of the supercapacitor is comparatively lower
  If the C-rate of the batteries creates a bottleneck, increase their capacity
S. Majumder, S. A. Khaparde, A. P. Agalgaonkar, S. V. Kulkarni, S. Perera, and P. Ciufo, “Hybrid storage system sizing for minimum daily variability injection,” in 2019 IEEE region ten symposium (TENSYMP), Kolkata, India, Jun. 2019.

## Slide 12: Problem 1C: Optimal Scheduling of a Wind Power Producer (WPP)
While DSOs as aggregators can provide the independent WPP visibility into the electricity market, their operational objectives are often conflicting
If DGs are non-collocated, performance of the distribution network, in terms of (i) network losses, (ii) voltage profile and (iii) overall energy efficiency, will improve
While improvement of network performance may not be an obligation for the WPPs, appropriate remuneration, or incentive to them is expected to improve the distribution network performance
Forecast-inaccuracy requires WPPs to procure reserve from self-owned units, which will directly affect their day-ahead energy schedule (not discussed in this presentation)
S. Majumder and S. A. Khaparde, “Revenue and ancillary benefit maximisation of multiple non-collocated wind power producers considering uncertainties,” IET Gen. Transm. Distrib., vol. 10, no. 3, pp. 789-797, July 2016.

## Slide 13: Locational Dependence
Observations:
  Appropriate remuneration is shown to actively modify the schedule
  Schedule also depends upon the location of the WPP in the network
  The heat-map shows that if the WTG and the BSD are placed relatively far away in the radial distribution network, the proposed strategy will generate maximum benefit
Notes: Fig. WTG_vary, profitmap

## Slide 14: Mitigation of Global Effects of Temporary Faults

## Slide 15: Challenges
Reduction in inertial reserve with increased penetration of inverter-interfaced generators (both for RE generators, and storage devices) will translate into a higher rate of change of frequency (RoCoF)
The traditional allowable delay in the provision of the unrewarded primary frequency reserve will be a risk for grid security
If an additional measuring and communication interface is in place, inverters can reach to their full output capability within a few seconds and the droop control can limit the post-contingency frequency excursion
Provision of local resources by the aggregator are invisible to the system operator, necessitating the requirement of enough reserve to contain the local contingencies a low-inertia system

## Slide 16: Problem 2A: Allowable Delay Heuristic Determination
The availability of a simple heuristic of the allowable delay will help the market operator to clear successful PFR providing entities:
The existence of exponential function in the delayed swing equation necessitates the use of Padé approximation to obtain the transfer function
Analytical expression obtained for different orders of approximation is:
is the allowable delay, is the approximation order, is the desired damping factor, is the inertial constant, is the aggregated regulation factor, is the system nominal frequency

## Slide 17: Validation of Heuristic Expression
  Convergence of higher order approximations are validated; order more than 2 is consistently good
Notes: Fig. Proof02, PadeHigher, Zeta_to_Alpha

## Slide 18: Problem 2B: Self-Scheduling of VPPs to Contain Temporary Faults
While an auto-recloser can recover the system from temporary faults and protect the rest of the system from the faulted section, the fault-clearing operation takes several seconds
Consequently, temporary disconnection of a section for automatic extinguishing can create a load-generation imbalance, which may trigger a frequency excursion event in a low-inertia system
This issue becomes significant in a system with a higher fault rate (e.g. during certain seasons of the year)
Therefore, the fast-reserve requirement is a function of the schedule of internal generating resources, and such requirements are invisible to the system operator
Therefore, it becomes a responsibility of the VPP (an aggregating DSO or utility) operator to allocate sufficient fast-reserve provision (necessitating self-scheduling)

## Slide 19: Unavailability of Local Fast Reserve
Observations:
  Although the risk of disconnection exists, the inexpensiveness of provision of local fast-reserve can be an attractive proposition
  Increasing the confidence-level increases reserve requirements while reducing profits
Notes: Fig. Reserve_Loss_Surf, Fast_Cost

## Slide 20: Mitigation of Local Effects of Temporary Faults

## Slide 21: Challenges
In order to utilize limited benevolent effects of Dynamic Voltage Restorers (DVRs), multiple customers may cooperate to form a symbiotic group for the provision of the mitigation solution
The existence of ‘economy of scale’ can act as a facilitator of this
Under such resource provision framework, participation needs to be voluntary, while the true utility requirement of the appropriators is generally unmonitored, inducing the existence of free-riders
However, the benefit of the DVR being exclusive to a finite set of customers, the free-riding behavior can be restricted
Additionally, proper distribution of utility prohibits unilateral free-riding by any of the participants
S. Majumder, S. A. Khaparde, V. Pradhan, S. V. Kulkarni, A. P. Agalgaonkar, S. Perera, and P. P. Ciufo, “A critical review on the methods for calculating the risk of process failure because of voltage sags,” in IEEE International Conference on Power System Technology (POWERCON), Wollongong, NSW, Oct. 2016.

## Slide 22: Problem 3A: Common Pool Resources (CPR) Good Theory for Voltage Sag Mitigation
Given a group of customers available within the network, sag mitigation solution using a DVR becomes simultaneously rivalrous and non-excludable
Rivalrousness: By proper segregation and suitably locating DVRs
Non-excludability: It is not possible to prevent free-riders (e.g., voltage improvement to downstream customers)
‘Free-ride proof core’ solution concept has been utilized to ensure unilateral coalition deviation proof-ness
S. Majumder, A. P. Agalgaonkar, S. A. Khaparde, P. P. Ciufo, S. Perera, and S. V. Kulkarni, “Allocation of Common-Pool Resources in an Unmonitored Open System,” IEEE Trans. Power Syst. (Early Access)

## Slide 23: Problem 3B: Multiple Cluster Formation in a CPR Good
Solution Concept (According to Game Theory) |  |  | 
Numerically calculated solution | 0.410 | 0.126 | 0.093
The Nucleous | 0.4096 | 0.1277 | 0.0920
The Shapley Value | 0.4096 | 0.1274 | 0.0923
If multiple independent contribution group formation is allowed, free-riders can be strategically eliminated from being benefited from the CPR provision
Notes: Fig. Cluster_DVR_B

## Slide 24: Conclusion
In the first part of the presentation, the sizing and operation of storage devices have been discussed to mitigate the effects of RE variability
In the second part of the presentation, reserve requirement and allowable delay in reserve provision are discussed to increase system resilience against temporary faults
The third part focuses on policies of procuring voltage sag mitigation devices and sharing their cost among customers
The first part of this joint-PhD work primarily was taken up at IIT Bombay
Upon the mutual agreement, and owing to the strong PQ background of UOW, the third part was realized with joint efforts of IIT Bombay and UoW
The second part connects the first and third research contributions
The success of this collaboration program leads the way towards future collaboration opportunities

## Slide 25: Thank you